{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":60,"n_cols":9,"rows_kept":60,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYA-DW1P-H-"]
[]
[]
[]
[]
["","","","","","EWYA009DAW1P-H-","EWYA011DAW1P-H-","EWYA014DAW1P-H-","EWYA016DAW1P-H-"]
["Skaņas spiediena līmenis","Dzesēšana","","Nom.","dBA","44.0","47.7","50.8","51.0"]
["Hidraulikas komponenti","Paplašināšanās trauks","","Apjoms","l","8","8","8","8"]
["Darbības amplitūda","Gaisa puse","Dzesēšana","Min.","°CDB","10","10","10","10"]
["","","","Maks.","°CDB","43","43","43","43"]
["","","Apsilde","Maks.","°CDB","25","25","25","25"]
["","","","Min.","°CDB","-25","-25","-25","-25"]
["","Ūdens puse","Apsilde","Min.","°CDB","9 (7)","9 (7)","9 (7)","9 (7)"]
["","","","Maks.","°CDB","60 (7)","60 (7)","60 (7)","60 (7)"]
["","","Dzesēšana","Maks.","°CDB","22","22","22","22"]
["","","","Min.","°CDB","5","5","5","5"]
["Dzesētāja padeve","Uz kontūru","","","kg","3.80","3.80","3.80","3.80"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","2.6","2.6","2.6","2.6"]
["Kompresors","Veids","","","","Hermētiski noblīvēts invertoru kompresors ar peldošo rotoru","Hermētiski noblīvēts invertoru kompresors ar peldošo rotoru","Hermētiski noblīvēts invertoru kompresors ar peldošo rotoru","Hermētiski noblīvēts invertoru kompresors ar peldošo rotoru"]
["","Uzsākšanas metode","","","","Pārveidotāja piedziņa","Pārveidotāja piedziņa","Pārveidotāja piedziņa","Pārveidotāja piedziņa"]
["","Daudzums","","","","1","1","1","1"]
["Gaisa siltuma mainītājs","Veids","","","","Ļoti efektīvs ribojums un caurules veids ar iebūvētu pakārtoto dzesētāju","Ļoti efektīvs ribojums un caurules veids ar iebūvētu pakārtoto dzesētāju","Ļoti efektīvs ribojums un caurules veids ar iebūvētu pakārtoto dzesētāju","Ļoti efektīvs ribojums un caurules veids ar iebūvētu pakārtoto dzesētāju"]
["Svars","Ierīce","","","kg","147","147","147","147"]
["EER","","","","","3.35 (1), 5.34 (2)","3.26 (1), 5.31 (2)","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["Refrigerant","GWP","","","","675.0","675.0","675.0","675.0"]
["","Tips","","","","R-32","R-32","R-32","R-32"]
["","Shēmas","","Daudzums","","1","1","1","1"]
["","Kontrole","","","","Elektroniskais izplešanās vārsts","Elektroniskais izplešanās vārsts","Elektroniskais izplešanās vārsts","Elektroniskais izplešanās vārsts"]
["Ventilatora motors","Ātrums","Dzesēšana","Nom.","apgr./min.","500","550","650","650"]
["","","Apsilde","Nom.","apgr./min.","400","450","550","650"]
["Dzesēšanas jauda","Nom.","","","kW","9.35 (1), 9.10 (2)","11.6 (1), 11.5 (2)","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Ūdens siltuma mainītājs","Ūdens daudzums","","","l","2","2","2","2"]
["","Minimālais ūdens daudzums sistēmā","","","l","50 (6)","50 (6)","50 (6)","50 (6)"]
["","Veids","","","","Plākšņu siltummainis","Plākšņu siltummainis","Plākšņu siltummainis","Plākšņu siltummainis"]
["Strāvas ievade","Dzesēšana","","Nom.","kW","2.79 (1), 1.71 (2)","3.56 (1), 2.17 (2)","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["","Apsilde","","Nom.","kW","1.91 (3), 2.43 (4)","2.18 (3), 2.68 (4)","2.46 (3), 3.42 (4)","3.53 (3), 4.56 (4)"]
["Sound power level","Dzesēšana","","Nom.","dBA","65.5","67.0","69.0","69.0"]
["COP","","","","","4.91 (3), 3.71 (4)","4.83 (3), 3.66 (4)","4.87 (3), 3.64 (4)","4.53 (3), 3.51 (4)"]
["Izmēri","Ierīce","","Platums","mm","1,380","1,380","1,380","1,380"]
["","","","Dziļums","mm","460","460","460","460"]
["","","","Augstums","mm","870","870","870","870"]
["Jaudas kontrole","Metode","","","","Mainīgs (pārveidotājs)","Mainīgs (pārveidotājs)","Mainīgs (pārveidotājs)","Mainīgs (pārveidotājs)"]
["Telpu apsilde","Mērena klimata ūdens izplūde 55°C","Vispārēji","Telpu apsildes sezonas efekt. klase","","A++","A++","A++","A++"]
["","","","ηs (telpu apsildes sezonas efektivitāte)","%","135","132","134","132"]
["","","","SCOP","","3.44","3.37","3.42","3.37"]
["Ventilators","Gaisa plūsmas ātrums","Apsilde","Nom.","m³/min.","48.0","55.8","70.4","85.0"]
["","","Dzesēšana","Nom.","m³/min.","63","70","85","85"]
["Apsildes jauda","Nom.","","","kW","9.37 (3), 9.00 (4)","10.6 (3), 9.82 (4)","12.0 (3), 12.5 (4)","16.0 (3), 16.0 (4)"]
["Kompresors","Uzsākšanas metode","","","","Pārveidotājs","Pārveidotājs","Pārveidotājs","Pārveidotājs"]
["Power supply","Phase","","","","3~","3~","3~","3~"]
["","Frekvence","","","Hz","50","50","50","50"]
["","Nosaukums","","","","W1","W1","W1","W1"]
["","Spriegums","","","V","400","400","400","400"]
["Notes","","","","","(1) - Dzesēšana: EW 12℃; LW 7℃; apkārtējie apstākļi: 35°CDB","(1) - Dzesēšana: EW 12℃; LW 7℃; apkārtējie apstākļi: 35°CDB","(1) - Dzesēšana: EW 12℃; LW 7℃; apkārtējie apstākļi: 35°CDB","(1) - Dzesēšana: EW 12℃; LW 7℃; apkārtējie apstākļi: 35°CDB"]
["","","","","","(2) - Dzesēšana: EW 23℃; LW 18℃; apkārtējie apstākļi: 35°CDB","(2) - Dzesēšana: EW 23℃; LW 18℃; apkārtējie apstākļi: 35°CDB","(2) - Dzesēšana: EW 23℃; LW 18℃; apkārtējie apstākļi: 35°CDB","(2) - Dzesēšana: EW 23℃; LW 18℃; apkārtējie apstākļi: 35°CDB"]
["","","","","","(3) - Nosacījums: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Nosacījums: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Nosacījums: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Nosacījums: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Nosacījums: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Nosacījums: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Nosacījums: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Nosacījums: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(5) - Saskaņās ar EN14825","(5) - Saskaņās ar EN14825","(5) - Saskaņās ar EN14825","(5) - Saskaņās ar EN14825"]
["","","","","","(6) - Atkarībā no darbības režīma; skatiet uzstādīšanas rokasgrāmatu","(6) - Atkarībā no darbības režīma; skatiet uzstādīšanas rokasgrāmatu","(6) - Atkarībā no darbības režīma; skatiet uzstādīšanas rokasgrāmatu","(6) - Atkarībā no darbības režīma; skatiet uzstādīšanas rokasgrāmatu"]
["","","","","","(7) - Papildu informācijai skatīt darbības diapazonu attēlu","(7) - Papildu informācijai skatīt darbības diapazonu attēlu","(7) - Papildu informācijai skatīt darbības diapazonu attēlu","(7) - Papildu informācijai skatīt darbības diapazonu attēlu"]