{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":74,"n_cols":9,"rows_kept":74,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZAG-MV1"]
[]
[]
[]
[]
["","","","","","RZAG71M7V1B","RZAG100M7V1B","RZAG125M7V1B","RZAG140M7V1B"]
["Skaņas spiediena līmenis","Apsilde","","Nom.","dBA","","","","52"]
["","Dzesēšana","","Nom.","dBA","","","","51"]
["Standard Accessories","Sasienamie iesaiņojumi","","","","","","","2"]
["","Uzstādīšanas rokasgrāmata","","","","","","","1"]
["","Dzesētāja uzlīme F gāzes regulācijai","","","","","","","1"]
["","Vispārēji drošības pasākumi","","","","","","","1"]
["","LOT10 enerģijas uzlīme","","","","","","","1"]
["Refrigerant","Charge","","","TCO2Eq","","","","2.53"]
["","GWP","","","","","","","675"]
["","Uzlāde","","","kg","","","","3.75"]
["","Type","","","","","","","R-32"]
["Cauruļvadu savienojumi","Šķidrums","","OD","mm","","","","9.52"]
["","Cauruļvadu garums","Maks.","Ārējā ierīce — iekštelpu ierīce","m","","","","85"]
["","","Sistēma","Neuzlādēts","m","","","","40"]
["","","","Ekvivalents","m","","","","100"]
["","Gāze","","OD","mm","","","","15.9"]
["","Līmeņa atšķirība","Iekštelpu ierīce-iekštelpu ierīce","Maks.","m","","","","0.5"]
["","","Iekštelpu ierīce – āra ierīce","Maks.","m","","","","30.0"]
["","Papildu dzesētāja uzlāde","","","kg/m","","","","Skatiet uzstādīšanas rokasgrāmatu"]
["Skaņas jaudas līmenis","Dzesēšana","","","dBA","","","","70"]
["","Apsilde","","","dBA","","","","70 (1)"]
["Kompresors","Type","","","","","","","Hermētiski noblīvēts šūpojošais kompresors"]
["Izmēri","Ierīce","","Width","mm","","","","940"]
["","","","Depth","mm","","","","320"]
["","","","Height","mm","","","","1,430"]
["Svars","Unit","","","kg","","","","92"]
["Power supply","Fāze","","","","","","","1~"]
["","Frekvence","","","Hz","","","","50"]
["","Spriegums","","","V","","","","220-240"]
["Notes","","","","","","","","(1) - Saskaņā ar ENER Lot 21"]
["","","","","","","","","(2) - Eiropas/starptautiskā tehniskā standarta limitu iestatījums saskaņotām strāvām, ko rada iekārta, kas savienota ar publiskās lietošanas zemsprieguma sistēmu ar ievades strāvu > 16 A un ≤ 75 A uz fāzi."]
["","","","","","","","","(3) - Ssc: Īssavienojuma strāva"]
["","","","","","","","","(4) - Eiropas/starptautiskā tehniskais standarts, kas nosaka ierobežojumus harmoniskām strāvām, ko rada iekārta, kas savienota ar koplietošanas zemsprieguma sistēmu ar ieejas strāvu > 16 A un <= 75 A uz fāzi."]
["Izmēri","Ierīce","","Augstums","mm","990","1430","1430"]
["","","","Platums","mm","940","940","940"]
["","","","Dziļums","mm","320","320","320"]
["Svars","Ierīce","","","kg","70","92","92"]
["Kompresors","Veids","","","","Hermētiski noblīvēts šūpojošais kompresors","Hermētiski noblīvēts šūpojošais kompresors","Hermētiski noblīvēts šūpojošais kompresors"]
["Darbības amplitūda","Dzesēšana","Apkārtējā vide","Min.","°CDB","-20","-20","-20"]
["","","","Maks.","°CDB","52","52","52"]
["","Apsilde","Apkārtējā vide","Min.","° CWB","-20","-20","-20"]
["","","","Maks.","° CWB","18.0","18.0","18.0"]
["Skaņas jaudas līmenis","Dzesēšana","","","dBA","64","66","69"]
["Skaņas spiediena līmenis","Dzesēšana","","Nom.","dBA","46","47","50"]
["","Apsilde","","Nom.","dBA","49","51","52"]
["Aukstumaģents","Tips","","","","R-32","R-32","R-32"]
["","Daudzums","","","kg","2.95","3.75","3.75"]
["","GWP","","","","675","675","675"]
["","Daudzums","","","tCO2Eq","1.99","2.53","2.53"]
["Cauruļu savienojumi","Šķidrums","","OD","mm","9.52","9.52","9.52"]
["","Gāze","","OD","mm","15.9","15.9","15.9"]
["Cauruļvadu savienojumi","Cauruļvadu garums","Maks.","Ārējā ierīce — iekštelpu ierīce","m","55","85","85"]
["","","Sistēma","Ekvivalents","m","75","100","100"]
["","","","Neuzlādēts","m","40","40","40"]
["","Papildu dzesētāja uzlāde","","","kg/m","Skatiet uzstādīšanas rokasgrāmatu","Skatiet uzstādīšanas rokasgrāmatu","Skatiet uzstādīšanas rokasgrāmatu"]
["","Līmeņa atšķirība","Iekštelpu ierīce – āra ierīce","Maks.","m","30.0","30.0","30.0"]
["","","Iekštelpu ierīce-iekštelpu ierīce","Maks.","m","0.5","0.5","0.5"]
["Standard Accessories","Installation manual","","","","1","1","1"]
["","Refrigerant label for F-gas regulation","","","","1","1","1"]
["","General safety precautions","","","","1","1","1"]
["","LOT10 Energy Label","","","","1","1","1"]
["","Tie-wraps","","","","2","2","2"]
["Barošanas avots","Fāze","","","","1~","1~","1~"]
["Strāvas padeve","Frekvence","","","Hz","50","50","50"]
["","Spriegums","","","V","220-240","220-240","220-240"]
["Strāva — 50Hz","Maks. drošinātāja ampēri (MFA)","","","A","20","32","32"]
["Skaņas jaudas līmenis","Apsilde","","","dBA","","","69 (1)"]
["Notes","","","","","","","(1) - Saskaņā ar ENER Lot 21"]