{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":54,"n_cols":7,"rows_kept":54,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZQ-C"]
[]
[]
[]
[]
["","","","","","RZQ200C7Y1B","RZQ250C7Y1B"]
["Izmēri","Ierīce","","Augstums","mm","1,680"]
["","","","Platums","mm","930"]
["","","","Dziļums","mm","765"]
["Svars","Ierīce","","","kg","183.0"]
["Compressor","Type","","","","Hermētiski noblīvēts spirālveida kompresors"]
["Darbības amplitūda","Dzesēšana","Apkārtējā vide","Min.","°CDB","-5.0"]
["","","","Maks.","°CDB","46.0"]
["","Apsilde","Apkārtējā vide","Min.","° CWB","-15.0"]
["","","","Maks.","° CWB","15.0"]
["Skaņas jaudas līmenis","Dzesēšana","","","dBA","78.0"]
["","Apsilde","","","dBA","78.0"]
["Refrigerant","Tips","","","","R-410A"]
["","Daudzums","","","kg","8.3"]
["","GWP","","","","2,087.5"]
["Cauruļu savienojumi","Šķidrums","","OD","mm","9.52"]
["","Gāze","","OD","mm","22.2"]
["","Cauruļvadu garums","Maks.","Ārējā ierīce — iekštelpu ierīce","m","100"]
["","","Sistēma","Neuzlādēts","m","30"]
["Standard Accessories","Uzstādīšanas rokasgrāmata","","","","1"]
["","Savienojuma cauruļvadi","","","","4"]
["Power supply","Fāze","","","","3N~"]
["","Frekvence","","","Hz","50"]
["","Spriegums","","","V","380-415"]
["Strāva - 50 Hz","Maks. drošinātāja ampēri (MFA)","","","A","25"]
["Notes","","","","","(1) - Strāvas padeve uz FDQ iekštelpu ierīci notiek atsevišķi"]
["","","","","","(2) - Elektrības datus skatiet atsevišķos zīmējumos"]
["Izmēri","Ierīce","","Augstums","mm","","1680"]
["","","","Platums","mm","","930"]
["","","","Dziļums","mm","","765"]
["Svars","Ierīce","","","kg","","184.0"]
["Kompresors","Veids","","","","","Hermētiski noblīvēts spirālveida kompresors"]
["Darbības amplitūda","Dzesēšana","Apkārtējā vide","Min.","°CDB","","-5.0"]
["","","","Maks.","°CDB","","46.0"]
["","Apsilde","Apkārtējā vide","Min.","° CWB","","-15.0"]
["","","","Maks.","° CWB","","15.0"]
["Skaņas jaudas līmenis","Dzesēšana","","","dBA","","78.0"]
["","Apsilde","","","dBA","","78.0"]
["Aukstumaģents","Daudzums","","","kg","","9.3"]
["","GWP","","","","","2087.5"]
["","Daudzums","","","tCO2Eq","","19.4"]
["Cauruļu savienojumi","Šķidrums","","OD","mm","","12.70"]
["","Gāze","","OD","mm","","22.2"]
["Cauruļvadu savienojumi","Cauruļvadu garums","Maks.","Ārējā ierīce — iekštelpu ierīce","m","","100"]
["","","Sistēma","Neuzlādēts","m","","30"]
["Standard Accessories","Installation manual","","","","","1"]
["","Connection pipes","","","","","4"]
["Strāvas padeve","Frekvence","","","Hz","","50"]
["Strāva — 50Hz","Maks. drošinātāja ampēri (MFA)","","","A","","25"]